## Sheet1 (hidden)
PRESSURE TEST & MAKEUP WATER FORM (As per ANSI/AWWA C605-13)
Project Number: | [8 empty] | Contractor:
Date: | [8 empty] | Location:
Test to be performed on PVC pipe for a duration of one hour using a water barrel that meets the specifications of the construction standards and has an internal diameter of 58cm.
Time (00:00) |  |  | Pressure (psi or kPa) |  |  |  |  | Water Level (cm) |  |  | Test Pressure, P (psi/kPa):
Total Change in Water Level, W (cm)=
Total Test Time, T (hours) =
Makeup Water Required (L) (Actual Leakage) | [14 empty] | L
Test Area:
Include on Drawing
○ Valve & Hydrant Numbers
○ Street Names
□ PASS | [9 empty] | □ FAIL
(Makeup Water Required < Makeup Water Allowance) | [9 empty] | (Makeup Water Required > Makeup Water Allowance)
PRESSURE TEST & MAKEUP WATER FORM (As per ANSI/AWWA C605-13)
Allowance Calculation
Diameter 1, D1: | [9 empty] | Diameter 2, D2:
Pipe Stick Length (PSL) : 3m pipe sticks 6m pipe sticks | [9 empty] | Pipe Stick Length (PSL) : 3m pipe sticks 6m pipe sticks
Fittings |  |  | # |  |  |  | Equivalent Length |  |  | Fittings |  |  | # |  |  |  | Equivalent Length
Cross |  |  |  | x | 3 x PSL = |  |  |  |  | Cross |  |  |  | x | 3 x PSL =
Tee |  |  |  | x | 2 x PSL = |  |  |  |  | Tee |  |  |  | x | 2 x PSL =
Valve (CVs incl.) |  |  |  | x | 1 x PSL = |  |  |  |  | Valve (CVs incl.) |  |  |  | x | 1 x PSL =
Bend/Coupling/Reducer |  |  |  | x | 1 x PSL = |  |  |  |  | Bend/Coupling/Reducer |  |  |  | x | 1 x PSL =
Hydrant |  |  |  | x | 1 x PSL = |  |  |  |  | Hydrant |  |  |  | x | 1 x PSL =
Other (plug/air vent/ flushpoint, etc.) |  |  |  | x | 1 x PSL = |  |  |  |  | Other (plug/air vent/ flushpoint, etc.) |  |  |  | x | 1 x PSL =
[6 empty] | Length of straight pipe = | [9 empty] | Length of straight pipe =
|  |  | Total Length, L1 = . | [9 empty] | Total Length, L2 = .
Makeup Water Allowance (L) (Allowable Leakage) | [9 empty] | Makeup Water Allowance (L) (Allowable Leakage)
[7 empty] | = | L | [7 empty] | = | L
Diameter 3, D3: | [9 empty] | Diameter 4, D4:
Pipe Stick Length (PSL) : 3m pipe sticks 6m pipe sticks | [9 empty] | Pipe Stick Length (PSL) : 3m pipe sticks 6m pipe sticks
Fittings |  |  | # |  |  |  | Equivalent Length |  |  | Fittings |  |  | # |  |  |  | Equivalent Length
Cross |  |  |  | x | 3 x PSL = |  |  |  |  | Cross |  |  |  | x | 3 x PSL =
Tee |  |  |  | x | 2 x PSL = |  |  |  |  | Tee |  |  |  | x | 2 x PSL =
Valve (CVs incl.) |  |  |  | x | 1 x PSL = |  |  |  |  | Valve (CVs incl.) |  |  |  | x | 1 x PSL =
Bend/Coupling/Reducer |  |  |  | x | 1 x PSL = |  |  |  |  | Bend/Coupling/Reducer |  |  |  | x | 1 x PSL =
Hydrant |  |  |  | x | 1 x PSL = |  |  |  |  | Hydrant |  |  |  | x | 1 x PSL =
Other (plug/air vent/ flushpoint, etc.) |  |  |  | x | 1 x PSL = |  |  |  |  | Other (plug/air vent/ flushpoint, etc.) |  |  |  | x | 1 x PSL =
[6 empty] | Length of straight pipe = | [9 empty] | Length of straight pipe =
|  | Total Length, L3 = . | [9 empty] | Total Length, L4 = .
Makeup Water Allowance (L) (Allowable Leakage) | [9 empty] | Makeup Water Allowance (L) (Allowable Leakage)
[7 empty] | = | L | [7 empty] | = | L
Add each diameter's allowance together to get total allowance:
Total Makeup Water Allowance (L): (Allowable Leakage) | [7 empty] | L
CONTRACTOR REP SIGNATURE:
EPCOR REP NAME:
EPCOR REP SIGNATURE:
=W×(π×((Inner Diameter ofBarrel)/2)^2)/1000=
=(L_1×D_1×√P)/795,000×T
=(L_2×D_2×√P)/795,000×T
=(L_3×D_3×√P)/795,000×T
=(L_4×D_4×√P)/795,000×T
Test pressure must remain within 5 psi of starting pressure (100 psi or 150 psi). If pressure falls more than 5 psi, pump water to bring pressure back up. Record the time, pressure and water level before and after water is added. If pressure remains the same over the course of test, only record start and end times and pressures.

## Cover Sheet
Hydrostatic Testing Report
for Water Infrastructure Installation
for EPCOR Water Services, Inc.
Servicing Agreement: |  |  |  | EPCOR Project Number:
Consultant: |  |  |  | Consultant Project Number:
Contractor: |  |  |  | Developer:
Subdivision: |  |  |  | Date:
I, |  |  | of the |  | Affix engineer or professional technologist seal here
firm
("Consulting Engineers") hereby certify that the following bacteriological and hydrostatic tests were carried out in accordance with the City of Edmonton Design and Construction Standards and AWWA Standard C200. All pressure gauges have been calibrated prior to testing in accordance with the requirements of the City of Edmonton Design and Construction Standards and the calibration certification has been attached to this report.
Diagram of test area

## Hydrostatic Test_PVC
Hydrostatic Testing Report for Jointed PVC Water Mains
for Water Infrastructure Installation
for EPCOR Water Services, Inc.
Report For:
Test to be performed on jointed PVC pipe as per the specifications of the Design and Construction Standards Volume 4 - Water.
Makeup Water Allowance Calculation
Quantity of Allowable Makeup Water is to be calculated with the following formula:
| Average Test Pressure, P (kPa): | [6 empty] | Total Test Time, T (hr):
| Nominal Pipe Diameter, D (mm) |  |  |  | Length of Pipe, L (m) |  |  | Quantity of Allowable Makeup Water, Qm, i (L)
| Sum each diameter's allowance together to get total allowance. |  |  |  |  | Total Makeup Water Allowance, Qm (L):
Actual Makeup Water Calculation
Quantity of Actual Makeup Water is to be calculated with the following formula:
| Time (00:00) |  |  | Pressure (kPa) |  | Water Level (cm) |  | Initial Test Pressure, Pi (kPa):
Total Change in Water Level, W (cm)=
Total Test Time, T (hours) =
Inner Diameter of Barrel, DB (cm) =
Actual Makeup Water Required, Qact (L):
| □ PASS | [5 empty] | □ FAIL (Retest required)
| (Makeup Water Required < Makeup Water Allowance) | [5 empty] | (Makeup Water Required > Makeup Water Allowance)
If test fails, list all required repairs and the schedule for completion:
CONSULTANT REP SIGNATURE:
CONTRACTOR REP SIGNATURE:
EPCOR REP NAME:
EPCOR REP SIGNATURE:
Q_act=W×(π×(D_B/2)^2)/1000
Test pressure must remain within 20 kPa of starting pressure. If pressure falls more than 20 kPa, pump water to bring pressure back up. Record the time, pressure and water level before and after water is added. If pressure remains the same over the course of test, only record start and end times and pressures.

## Hydrostatic Test_Steel
Hydrostatic Testing Report for Welded Steel Water Mains
for Water Infrastructure Installation
for EPCOR Water Services, Inc.
Report For:
Test to be performed on welded steel pipe as per the specifications of the Design and Construction Standards Volume 4 - Water.
Makeup Water Allowance
There is no allowed leakage for the testing of welded steel water mains. If leakage occurs, correct the deficiencies and repeat hydrostatic testing.
Pressure Log
Record the pressure of the hydrostatic test at the beginning of the test, at 20 minute intervals during the test and at the end of the test. The test pressure must remain within 20kPa of starting pressure. If the pressure does not remain within 20 kPa of starting pressure, the hydrostatic test has failed.
| Initial Test Pressure, Pi (kPa): |  |  | Allowable Pressure Range (kPa):
|  | Interval | Time (00:00) | Pressure (kPa) |  | Pass? (Y/N)
Start
1
2
3
4
5
6
7
8
9
10
11
12
End
| □ PASS |  |  |  | □ FAIL (Retest required)
If test fails, list all required repairs and the schedule for completion:
CONSULTANT REP SIGNATURE:
CONTRACTOR REP SIGNATURE:
EPCOR REP NAME:
EPCOR REP SIGNATURE:

## Hydrostatic Testing_Hydrants
Hydrostatic Testing Report for Hydrants
for Water Infrastructure Installation
for EPCOR Water Services, Inc.
| Report For: |  |  |  |  | Page: |  | of
Test to be performed on each hydrant as per the specifications of the Design and Construction Standards Volume 4 - Water.
| Hydrant Number | Date | Test Pressure (kPa) | Leaks observed during Hydrostatic Test? (Y/N) | Does the hydrant have sufficient suction during drainage test? (Y/N) |  | PASS? (Y/N) | If test fails, list all required repairs and schedule to complete
CONSULTANT REP SIGNATURE:
CONTRACTOR REP SIGNATURE:
EPCOR REP SIGNATURE:

## PRINT (hidden)
Hydrostatic Testing Report
for Water Infrastructure Installation
for EPCOR Water Services, Inc.
Servicing Agreement: | [10 empty] | EPCOR Project Number:
Consultant: | [10 empty] | Consultant Project Number:
Contractor: | [10 empty] | Developer:
Subdivision: | [10 empty] | Date:
Test to be performed on jointed PVC pipe as per the specifications of the Design and Construction Standards Volume 4 - Water.
Makeup Water Allowance Calculation
If a fitting has multiple diameters, use the main line diameter or the smaller diameter. e.g. use 300mm for a 300-150 tee, use 200mm for a 250-200 coupling or reducer, use 200mm for a 200-300 cross.
| Diameter 1, D1: | [10 empty] | Diameter 2, D2:
| Pipe Stick Length (PSL) : □ 3m pipe sticks □ 6m pipe sticks | [10 empty] | Pipe Stick Length (PSL) : □ 3m pipe sticks □ 6m pipe sticks
| Fittings |  |  |  | # |  |  |  | Equivalent Length |  |  | Fittings |  |  |  | # |  |  |  | Equivalent Length
| Cross |  |  |  |  | x | 3 x PSL = |  |  |  |  | Cross |  |  |  |  | x | 3 x PSL =
| Tee |  |  |  |  | x | 2 x PSL = |  |  |  |  | Tee |  |  |  |  | x | 2 x PSL =
| Valve (CVs incl.) |  |  |  |  | x | 1 x PSL = |  |  |  |  | Valve (CVs incl.) |  |  |  |  | x | 1 x PSL =
| Bend/Coupling/Reducer |  |  |  |  | x | 1 x PSL = |  |  |  |  | Bend/Coupling/Reducer |  |  |  |  | x | 1 x PSL =
| Hydrant |  |  |  |  | x | 1 x PSL = |  |  |  |  | Hydrant |  |  |  |  | x | 1 x PSL =
| Other (plug/air vent/ flushpoint, etc.) |  |  |  |  | x | 1 x PSL = |  |  |  |  | Other (plug/air vent/ flushpoint, etc.) |  |  |  |  | x | 1 x PSL =
[8 empty] | Length of straight pipe (m) = | [10 empty] | Length of straight pipe (m) =
|  |  | Total Length, L1 (m) = | [10 empty] | Total Length, L2 (m) =
| Makeup Water Allowance (L) (Allowable Leakage) | [10 empty] | Makeup Water Allowance (L) (Allowable Leakage)
[9 empty] | = | L | [8 empty] | = | L
| Diameter 3, D3: | [10 empty] | Diameter 4, D4:
| Pipe Stick Length (PSL) : □ 3m pipe sticks □ 6m pipe sticks | [10 empty] | Pipe Stick Length (PSL) : □ 3m pipe sticks □ 6m pipe sticks
| Fittings |  |  |  | # |  |  |  | Equivalent Length |  |  | Fittings |  |  |  | # |  |  |  | Equivalent Length
| Cross |  |  |  |  | x | 3 x PSL = |  |  |  |  | Cross |  |  |  |  | x | 3 x PSL =
| Tee |  |  |  |  | x | 2 x PSL = |  |  |  |  | Tee |  |  |  |  | x | 2 x PSL =
| Valve (CVs incl.) |  |  |  |  | x | 1 x PSL = |  |  |  |  | Valve (CVs incl.) |  |  |  |  | x | 1 x PSL =
| Bend/Coupling/Reducer |  |  |  |  | x | 1 x PSL = |  |  |  |  | Bend/Coupling/Reducer |  |  |  |  | x | 1 x PSL =
| Hydrant |  |  |  |  | x | 1 x PSL = |  |  |  |  | Hydrant |  |  |  |  | x | 1 x PSL =
| Other (plug/air vent/ flushpoint, etc.) |  |  |  |  | x | 1 x PSL = |  |  |  |  | Other (plug/air vent/ flushpoint, etc.) |  |  |  |  | x | 1 x PSL =
[8 empty] | Length of straight pipe (m) = | [10 empty] | Length of straight pipe (m) =
|  |  |  | Total Length, L3 (m) = | [10 empty] | Total Length, L4 (m) =
| Makeup Water Allowance (L) (Allowable Leakage) | [10 empty] | Makeup Water Allowance (L) (Allowable Leakage)
[9 empty] | = | L | [8 empty] | = | L
| Total Makeup Water Allowance (L): (Allowable Leakage) | [8 empty] | L
Hydrostatic Testing Report
for Water Infrastructure Installation
for EPCOR Water Services, Inc.
| Time (00:00) |  |  |  | Pressure (kPa) |  |  |  |  | Water Level (cm) |  |  | Test Pressure, P (kPa):
Total Change in Water Level, W (cm)=
Total Test Time, T (hours) =
Inner Diameter of Barrel (cm) =
| Makeup Water Required (L) (Actual Leakage) | [16 empty] | L
| Instructions: |  |  | Include all items required on hydrostatic testing plan in drawing. Attach pressure gauge calibration results.
Test Area:
| □ PASS | [10 empty] | □ FAIL (Retest required)
| (Makeup Water Required < Makeup Water Allowance) | [10 empty] | (Makeup Water Required > Makeup Water Allowance)
CONSULTANT REP SIGNATURE:
CONTRACTOR REP SIGNATURE:
EPCOR REP NAME:
EPCOR REP SIGNATURE:
=(L_1×D_1×√P)/795,000×T
=(L_2×D_2×√P)/795,000×T
=(L_3×D_3×√P)/795,000×T
=(L_4×D_4×√P)/795,000×T
=W×(π×((Inner Diameter ofBarrel (cm))/2)^2)/1000=
Test pressure must remain within 20 kPa of starting pressure. If pressure falls more than 20 kPa, pump water to bring pressure back up. Record the time, pressure and water level before and after water is added. If pressure remains the same over the course of test, only record start and end times and pressures.
Add each diameter's allowance together to get total allowance.

## ONLINE (hidden)
PRESSURE TEST & MAKEUP WATER FORM
| Project Number: | [5 empty] | Contractor:
| Date: | [5 empty] | Consultant:
| Location: | [5 empty] | Developer:
Test to be performed on jointed PVC pipe as per the specifications of the Design and Construction Standards Volume 4 - Water.
Makeup Water Allowance Calculation
If a fitting has multiple diameters, use the main line diameter or the smaller diameter. e.g. use 300mm for a 300-150 tee, use 200mm for a 250-200 coupling or reducer, use 200mm for a 200-300 cross.
| Diameter 1 (mm), D1: | [6 empty] | Diameter 2 (mm), D2:
|  |  |  | Pipe Stick Length : | [7 empty] | Pipe Stick Length :
| Fitting |  | # |  |  |  |  | Fitting |  |  | #
| Cross |  |  | Length of straight pipe: |  |  |  | Cross |  |  |  | Length of straight pipe:
| Tee | [6 empty] | Tee
| Valve (CVs incl.) |  |  | Total Length: |  |  |  | Valve (CVs incl.) |  |  |  | Total Length:
| Bend/Coupling/ Reducer |  |  | 0 |  |  |  | Bend/Coupling/ Reducer |  |  |  | 0
| Hydrant |  |  | Allowance (L) |  |  |  | Hydrant |  |  |  | Allowance (L)
| Other (plug/air vent/ flushpoint, etc.) |  |  | 0 |  |  |  | Other (plug/air vent/ flushpoint, etc.) |  |  |  | 0
| Diameter 3 (mm), D3: | [6 empty] | Diameter 4 (mm), D4:
|  |  |  | Pipe Stick Length : | [7 empty] | Pipe Stick Length :
| Fitting |  | # |  |  |  |  | Fitting |  |  | #
| Cross |  |  | Length of straight pipe: |  |  |  | Cross |  |  |  | Length of straight pipe:
| Tee | [6 empty] | Tee
| Valve (CVs incl.) |  |  | Total Length: |  |  |  | Valve (CVs incl.) |  |  |  | Total Length:
| Bend/Coupling/ Reducer |  |  | 0 |  |  |  | Bend/Coupling/ Reducer |  |  |  | 0
| Hydrant |  |  | Allowance (L) |  |  |  | Hydrant |  |  |  | Allowance (L)
| Other (plug/air vent/ flushpoint, etc.) |  |  | 0 |  |  |  | Other (plug/air vent/ flushpoint, etc.) |  |  |  | 0
| Total Makeup Water Allowance (L): (Allowable Leakage) |  |  |  |  | 0 |  | L
PRESSURE TEST & MAKEUP WATER FORM
| Time (00:00) |  | Pressure (kPa) |  |  | Water Level (cm) |  |  |  | Test Pressure, P (kPa):
Total Change in Water Level, W (cm)=
Total Test Time, T (hours) =
|  | Inner Diameter of Barrel (cm) = | [6 empty] | Makeup Water Required (L) (Actual Leakage) |  |  |  | 0 | L
Test Area:
Include on Drawing
○ Valve & Hydrant Numbers
○ Street Names
○ Pump Location
NOT ENOUGH DATA
NOT ENOUGH DATA
CONSULTANT REP SIGNATURE:
CONTRACTOR REP SIGNATURE:
EPCOR REP NAME:
EPCOR REP SIGNATURE:
Test pressure must remain within 20 kPa of starting pressure. If pressure falls more than 20 kPa, pump water to bring pressure back up. Record the time, pressure and water level before and after water is added. If pressure remains the same over the course of test, only record start and end times and pressures.

## PRINT_EXAMPLE (hidden)
PRESSURE TEST & MAKEUP WATER FORM
| Project Number: |  |  | WXX-YYXX | [5 empty] | Contractor: | Name of Contractor
| Date: |  | 2020-08-17 | [6 empty] | Consultant: | N/A
| Location: |  | LW 79 ST - 80 AVE to 81 AVE | [6 empty] | Developer: | N/A
Test to be performed on jointed PVC pipe as per the specifications of the Design and Construction Standards Volume 4 - Water.
Makeup Water Allowance Calculation
If a fitting has multiple diameters, use the main line diameter or the smaller diameter. e.g. use 300mm for a 300-150 tee, use 200mm for a 250-200 coupling or reducer, use 200mm for a 200-300 cross.
| Diameter 1, D1: |  |  | 250 mm | [6 empty] | Diameter 2, D2: |  | 150mm
| Pipe Stick Length (PSL) : □ 3m pipe sticks □ 6m pipe sticks | [9 empty] | Pipe Stick Length (PSL) : □ 3m pipe sticks □ 6m pipe sticks
| Fittings |  |  | # |  |  |  | Equivalent Length |  |  | Fittings |  | # |  |  |  | Equivalent Length
| Cross |  |  |  | x | 3 x PSL = |  |  |  |  | Cross |  |  | x | 3 x PSL =
| Tee |  |  | 2 | x | 2 x PSL = |  | 24m |  |  | Tee |  |  | x | 2 x PSL =
| Valve (CVs incl.) |  |  | 2 | x | 1 x PSL = |  | 12m |  |  | Valve (CVs incl.) |  | 2 | x | 1 x PSL = |  | 6m
| Bend/Coupling/Reducer |  |  | 2 | x | 1 x PSL = |  | 12m |  |  | Bend/Coupling/Reducer |  |  | x | 1 x PSL =
| Hydrant |  |  |  | x | 1 x PSL = |  |  |  |  | Hydrant |  | 2 | x | 1 x PSL = |  | 6m
| Other (plug/air vent/ flushpoint, etc.) |  |  |  | x | 1 x PSL = |  |  |  |  | Other (plug/air vent/ flushpoint, etc.) |  |  | x | 1 x PSL =
[7 empty] | Length of straight pipe = | 320m | [7 empty] | Length of straight pipe = | 7m
|  |  | Total Length, L1 (metres) = |  |  |  |  | 378m |  |  |  | Total Length, L2 (metres) = |  |  |  |  | 19m
| Makeup Water Allowance (L) (Allowable Leakage) | [9 empty] | Makeup Water Allowance (L) (Allowable Leakage)
[8 empty] | = | 3.12 L | [6 empty] | = | 0.0942 L
| Diameter 3, D3: |  |  | N/A | [6 empty] | Diameter 4, D4: |  | N/A
| Pipe Stick Length (PSL) : □ 3m pipe sticks □ 6m pipe sticks | [9 empty] | Pipe Stick Length (PSL) : □ 3m pipe sticks □ 6m pipe sticks
| Fittings |  |  | # |  |  |  | Equivalent Length |  |  | Fittings |  | # |  |  |  | Equivalent Length
| Cross |  |  |  | x | 3 x PSL = |  |  |  |  | Cross |  |  | x | 3 x PSL =
| Tee |  |  |  | x | 2 x PSL = |  |  |  |  | Tee |  |  | x | 2 x PSL =
| Valve (CVs incl.) |  |  |  | x | 1 x PSL = |  |  |  |  | Valve (CVs incl.) |  |  | x | 1 x PSL =
| Bend/Coupling/Reducer |  |  |  | x | 1 x PSL = |  |  |  |  | Bend/Coupling/Reducer |  |  | x | 1 x PSL =
| Hydrant |  |  |  | x | 1 x PSL = |  |  |  |  | Hydrant |  |  | x | 1 x PSL =
| Other (plug/air vent/ flushpoint, etc.) |  |  |  | x | 1 x PSL = |  |  |  |  | Other (plug/air vent/ flushpoint, etc.) |  |  | x | 1 x PSL =
[7 empty] | Length of straight pipe = | [8 empty] | Length of straight pipe =
|  | Total Length, L3 (metres) = | [9 empty] | Total Length, L4 (metres)=
| Makeup Water Allowance (L) (Allowable Leakage) | [9 empty] | Makeup Water Allowance (L) (Allowable Leakage)
[8 empty] | = | L | [6 empty] | = | L
| Total Makeup Water Allowance (L): (Allowable Leakage) | [7 empty] | 3.21 L
PRESSURE TEST & MAKEUP WATER FORM
| Time (00:00) |  |  | Pressure (psi or kPa) |  |  |  |  | Water Level (cm) |  |  | Test Pressure, P (psi/kPa): |  |  |  |  | 690kPa
| 14:45 |  |  | 696 kPa |  |  |  |  | 24
| 14:50 |  |  | 676 kPa |  |  |  |  | 24
| 14:51 |  |  | 696 kPa |  |  |  |  | 26
| 15:45 |  |  | 694 kPa |  |  |  |  | 26.5
[8 empty] | Total Change in Water Level, W (cm)= | 2.5
|  | Total Test Time, T (hours) = | [6 empty] | 1
|  | Inner Diameter of Barrel (cm) = | [6 empty] | 57cm
| Makeup Water Required (L) (Actual Leakage) | [13 empty] | 6.38 L
Test Area:
Include on Drawing
○ Valve & Hydrant Numbers
○ Street Names
○ Pump Location
| □ PASS | [9 empty] | □ FAIL (Retest required)
| (Makeup Water Required < Makeup Water Allowance) | [9 empty] | (Makeup Water Required > Makeup Water Allowance)
CONSULTANT REP SIGNATURE: | [8 empty] | N/A
CONTRACTOR REP SIGNATURE: | [8 empty] | CONTRACTOR REP SIGNATURE
EPCOR REP NAME: | [8 empty] | EPCOR REP NAME
EPCOR REP SIGNATURE: | [8 empty] | EPCOR REP SIGNATURE
=(L_1×D_1×√P)/795,000×T
=(L_2×D_2×√P)/795,000×T
=(L_3×D_3×√P)/795,000×T
=(L_4×D_4×√P)/795,000×T
=W×(π×((Inner Diameter ofBarrel)/2)^2)/1000=
Test pressure must remain within 20 kPa of starting pressure. If pressure falls more than 20 kPa, pump water to bring pressure back up. Record the time, pressure and water level before and after water is added. If pressure remains the same over the course of test, only record start and end times and pressures.
Add each diameter's allowance together to get total allowance.
80 AVE
81 AVE
LW 79 ST
250 PVC
V123
V124
H567
V7655
H568
V7656
N/A

## ONLINE_EXAMPLE (hidden)
PRESSURE TEST & MAKEUP WATER FORM
| Project Number: |  |  | WXX-YYXX |  |  |  |  | Contractor: | Whissell Contracting Ltd.
| Date: |  | 2020-08-17 | [5 empty] | Consultant: | N/A
| Location: |  | LW 79 ST - 80 Ave to 81 AVE | [5 empty] | Developer: | N/A
Test to be performed on jointed PVC pipe as per the specifications of the Design and Construction Standards Volume 4 - Water.
Makeup Water Allowance Calculation
If a fitting has multiple diameters, use the main line diameter or the smaller diameter. e.g. use 300mm for a 300-150 tee, use 200mm for a 250-200 coupling or reducer, use 200mm for a 200-300 cross.
| Diameter 1 (mm), D1: |  |  |  | 250 |  |  |  |  | Diameter 2 (mm), D2: |  |  | 150
[6 empty] | Pipe Stick Length : | [7 empty] | Pipe Stick Length :
| Fitting |  |  | # |  | 6m sticks |  |  |  | Fitting |  | # |  | 3m sticks
| Cross |  |  |  |  | Length of straight pipe: |  |  |  | Cross |  |  |  | Length of straight pipe:
| Tee |  |  | 2 |  | 330 |  |  |  | Tee |  |  |  | 7
| Valve (CVs incl.) |  |  | 2 |  | Total Length: |  |  |  | Valve (CVs incl.) |  | 2 |  | Total Length:
| Bend/Coupling/ Reducer |  |  | 2 |  | 378 |  |  |  | Bend/Coupling/ Reducer |  |  |  | 19
| Hydrant |  |  |  |  | Allowance (L) |  |  |  | Hydrant |  | 2 |  | Allowance (L)
| Other (plug/air vent/ flushpoint, etc.) |  |  |  |  | 3.82 |  |  |  | Other (plug/air vent/ flushpoint, etc.) |  |  |  | 0.12
| Diameter 3 (mm), D3: | [8 empty] | Diameter 4 (mm), D4:
[6 empty] | Pipe Stick Length : | [7 empty] | Pipe Stick Length :
| Fitting |  |  | # |  | 3m sticks |  |  |  | Fitting |  | # |  | 3m sticks
| Cross |  |  |  |  | Length of straight pipe: |  |  |  | Cross |  |  |  | Length of straight pipe:
| Tee | [8 empty] | Tee
| Valve (CVs incl.) |  |  |  |  | Total Length: |  |  |  | Valve (CVs incl.) |  |  |  | Total Length:
| Bend/Coupling/ Reducer |  |  |  |  | 0 |  |  |  | Bend/Coupling/ Reducer |  |  |  | 0
| Hydrant |  |  |  |  | Allowance (L) |  |  |  | Hydrant |  |  |  | Allowance (L)
| Other (plug/air vent/ flushpoint, etc.) |  |  |  |  | 0 |  |  |  | Other (plug/air vent/ flushpoint, etc.) |  |  |  | 0
| Total Makeup Water Allowance (L): (Allowable Leakage) | [6 empty] | 3.94 |  | L
PRESSURE TEST & MAKEUP WATER FORM
| Time (00:00) |  |  | Pressure (kPa) |  |  |  | Water Level (cm) |  |  | Test Pressure, P (kPa): |  |  |  | 690kPa
| 14:45 |  |  | 696 kPa |  |  |  | 24
| 14:50 |  |  | 676 kPa |  |  |  | 24
| 14:51 |  |  | 696 kPa |  |  |  | 26
| 15:45 |  |  | 694 kPa |  |  |  | 26.5
[7 empty] | Total Change in Water Level, W (cm)= | 2.5
|  | Total Test Time, T (hours) = | [5 empty] | 1
|  | Inner Diameter of Barrel (cm) = | [5 empty] | 57 |  |  | Makeup Water Required (L) (Actual Leakage) |  |  |  | 6.38 | L
Test Area:
Include on Drawing
○ Valve & Hydrant Numbers
○ Street Names
○ Pump Location
PRESSURE TEST FAILED - Inspect infrastructure and restart pressure test.
(Makeup Water Required < Makeup Water Allowance)
CONSULTANT REP SIGNATURE: | [7 empty] | N/A
CONTRACTOR REP SIGNATURE: | [7 empty] | CONTRACTOR REP SIGNATURE
EPCOR REP NAME: | [7 empty] | EPCOR REP NAME
EPCOR REP SIGNATURE: | [7 empty] | EPCOR REP SIGNATURE
Test pressure must remain within 20 kPa of starting pressure. If pressure falls more than 20 kPa, pump water to bring pressure back up. Record the time, pressure and water level before and after water is added. If pressure remains the same over the course of test, only record start and end times and pressures.
80 AVE
81 AVE
LW 79 ST
250 PVC
V123
V124
H567
V7655
H568
V7656
N/A

## Data (hidden)
Test Pressure | Contractor | Pipe Sections | Diameter |  | Equivalent Length
690kPa | GS Holdings Company Ltd. | 3m sticks | N/A |  | 3m sticks | 6m sticks
1034kPa | M.A.P. Water & Sewer Services Ltd. | 6m sticks | 100 | Tee (2 sticks) | 6 | 12
| Whissell Contracting Ltd. |  | 150 | Cross (3 sticks) | 9 | 18
|  |  | 200 | Valve (1 stick) | 3 | 6
|  |  | 250 | Bend (1 stick) | 3 | 6
|  |  | 300 | Hydrant (1 stick) | 3 | 6
|  |  | 350 | Coupling/Reducer (1 stick) | 3 | 6
|  |  | 400 | Other (1 stick) (plug/air vent/ flushpoint, etc.) | 3 | 6
|  |  | 450 |  | 3 | 6
500
600
750
900